## DataSheet
ADNOC GAS DBOOM WORKS FOR RENTAL COMPRESSION FACILITIES FOR BUHASA PLANT (PROJECT 5.0)
| ADNOC DOCUMENT NO: DOD-30201-50150-BH-000-16-00-004 CONTRACTOR DOCUMENT NO: ADN-AEC-EL-DAT-009 | Rev.: A
DATASHEET - GAS POWER GENERATOR
Sr. No. | DESCRIPTION | Project Requirements | Data Filled By Vendor
1 | GENERAL
1.1 | Gas Generator Quantity | 02 | 2
1.2 | Gas Generator Tags | G-4101-01A/B | As per KAN Nameplate
1.3 | Make & Model Number of Alternator | VTA | Mecc alte ECO43 2S4A
1.4 | Country of Origin of Alternator | VTA | Italy/UK/China
1.5 | Make & Model Number of Engine | VTA | MAN E3872 LE201
1.6 | Country of Origin of Engine | VTA | Germany
1.7 | Acoustic & Weatherproof enclosure | Required | Yes
1.8 | CO2 Fire Suppressing System as per NFPA | Required | Yes
1.9 | Design Life | 06 years | 60 - 80k as per pipeline gas quality
1.10 | International Codes and Standards [Refer: Attachment-1] | Compliance Required As Applicable | OEM Standard Compliance (we cannot comply all standards given in the attachment-1)
1.11 | Vendor Deviation Form [Refer Attachment-2] | Vendor shall fill in the attached form in case of any deviation | Noted
1.12 | Site Conditions [Refere Attachment-3] | Compliance Required As Applicable | Noted
1.13 | Vendor Documents List [Refer Attachment-4] | Compliance Required | Will be provided later upon finalization and issuance of LOI
1.14 | Gas Gensets Operation: Parallel Generator Control Relay shall have provision of manual and automatic switching from one unit to the other after defined time | Compliance Required | Complied
2 | SITE & INSTALLATION CONDITION
2.1 | Area of Installation (Indoor/Outdoor) | Outdoor | Noted
2.2 | Area of Classification (Hazardous / Safe Area) | Safe Area | Noted
2.3 | Design Ambient Temperature - Maximum | 58 Deg C | Complied
2.4 | Design Ambient Temperature - Minimum | 05 Deg C | Complied
2.5 | Altitude Above Mean Sea Level | Less than 1000 meters | Complied
2.6 | Ambient Conditions | Dusty & humid | Noted
3 | DESIGN PARAMETERS FOR ENGINE
3.1 | Type of Design | VTA | 12 Cylinder, V - type (90°)
3.2 | Applicable Standard | ISO | ISO 9001:2015; ISO 8528
3.3 | Rated Continuous Power at Site Ambient Temperature (kW) | 525 kW @ 0.8 pf | 525 kW
3.4 | Rated Speed (RPM) | VTA | 1500
3.5 | Number of Strokes | VTA | 4
3.6 | Direction of Rotation from Drive End | CCW | CCW
3.7 | Overload Capability | 110% of Rated Power | N/A (These are continous rating sets 110% of overload capacity is not available)
3.8 | Exhaust Gas temperature:
3.9 | a) At outlet of cylinder | VTA | Refer to Engine datasheet
3.1 | b) Upstream turbo charger | VTA | 375 degC
3.11 | Cooling System | Air Cooled Horizontal Radiator or alternate as per Vendor Design | Air Cooled Horizontal Radiator
3.12 | Type of Starting Mechanism | Electric Start with Battery Backup | Electric Start with Battery
3.13 | Maximum Noise Level measured at 1 Meter distance from the enclosure | 85 dB (A) | 85 dB (A)
3.14 | Time Required for Start from Cold Conditions | VTA | 5 - 10 SEC
3.15 | Type of Fuel | Fuel Gas H2S Content: 50 ppm | Required Sulphur content is <60mg/Nm3 and Hydrogen sulphide is <20ppm/<30mg / Nm³
3.16 | Fuel Consumption at Rated Voltage | VTA | MJ/kWh 8.19
3.17 | Cylinder Arrangement | VTA | V - type (90°)
3.18 | Bore, mm | VTA | 138
3.19 | Compression Ratio | VTA | 13.3:1
3.2 | Instruments: Orifice Type Fuel Gas Metering Instrument [Separate for each unit] Lube Oil Hight Temperature Over Speed Vibration Lube Oil Temperature Others As per Vendor Standard Design & Monitoring and Protection | Required | Turbine Type Fuel Gas Metering Instrument, Knock sensing system available instead of vibration instruments. (Rest complied)
3.21 | Control: Mechanical Tachometer Lube Oil Pressure Gauge Water Temperature Gauge Running Manifold Vaccum Gauge Running Time Meter Start/Stop Control Exhaust Gas Temperature Cooling Water Pressure Others As per Vendor Standard Design | Required | Mechanical Techometer and Cooling Water Pressure not available, Rest complied and will be displayed by ALL IN ONE controller
3.22 | All measurements and control shall be provided to the DCS through redundant RS485 communication link | Required | Redundancy is not availble only RS485 is available
3.23 | Lube Oil System | Required | Complied
3.24 | Engine Exhaust System with Silencer | Required | Complied
3.25 | Shaft Couplings | Required | Direct coupled
3.26 | Torsional Analysis of Engine | Required | Torsion vibration compatability will be provided later on upon finalization
4 | FUEL GAS
4.1 | Fuel Gas Pressure | 7 barg | Noted
4.2 | Min / Max Pressure | VTA | 200/ 10000 mbar
4.3 | Size of fuel line | VTA | DN60 & DN80
4.4 | Emergency push button | VTA | Manual and electric Shut off valve will be available
4.5 | Lubrication consumption | VTA | 40 g/h
4.6 | Maximum Number of Continuous Operating Hours without maintenance interval (Hours) | VTA | 1500 - 2000 hrs depending on oil analysis report for lube oil degradation + oil contamination
4.7 | Duration of Shutdown for Routine maintenance after above Interval | VTA | 6 - 8 hrs
4.8 | Starting type | VTA | Electric
4.9 | NOx after SCR (selective catalytic reduction treatment | As per Scope of Work | 100mg/nm3 (Natural Gas) 200mg/nm3 (Fuel Gas)
4.10 | Exhaust Gas Treatment System | Incompliance to Sox Nox Project Specification, if required | SCR Treatment System with AdBlue tank for Nox and Carbonmono oxide
5 | DESIGN PARAMETERS - ALTERNATORS
5.1 | Rating capacity | 525 kW@ 58 Deg C | 680kW
5.2 | Rated Voltage (V) | 415V | 415V
5.3 | Rated current | VTA | 912 Amps
5.4 | Number of Phases | 3P+4W | Complied
5.5 | Rated Power Factor | 0.8 | Complied
5.6 | Rated Frequency (Hz) | 50 | Complied
5.7 | Rated Speed | VTA | 1500 rpm
5.8 | Stator Connection | Star Connection | Complied
5.9 | Generator Duty | S1 | Complied
5.10 | Rotation facing Drive End | VTA | CCW
5.11 | Winding Insulation- Generator & Exciter | Class H | Complied
5.12 | Protection method | IP 23 | Complied*
5.13 | Temperature rise | Class F | Class F
5.14 | Overload Capability | VTA | 110% of Rated Power
5.15 | Generator Efficiency (%) - at unity power factor: | VTA | 96%
5.16 | 3 Phase short circuit withstand time | 3s | 3s
5.17 | Recovery time to rated voltage | VTA | 20 - 30 Sec
5.18 | Speed control | Electronic Governor | Complied
5.19 | Type of Excitation Self excitation, Brushless type, consisting of a main AC exciter and a permanent magnet generator direct coupled and air cooled | Required | Self Excited PMG
5.20 | Excitation - Rated Current At least 110% of the excitation current at the rated output of the generator under the most stringent operating conditions | Required | Complied
5.21 | Excitation - Rated Voltage At least 110% of the rotor voltage at the rated output of the generator under the most stringent conditions | Required | Complied
5.22 | Winding temperature detectors (No & type) | 2 RTD per Phase, PT-100 platinum resistance elements as per IEC | PT100 will be provided (two on each phase)
5.23 | Bearing temperature detectors (No & type) | 2 RTD per Phase, PT-100 platinum resistance elements as per IEC | PT100 will be provided (one on bearing)
5.24 | Common Engine / Generator control panel | Required | Sync Control panels
5.25 | AMF [Auto Main Failure] Panel | Integrated with Control Panel or Separate as per Vendor standard design | Available
5.26 | Design Temperature (°C) | 58 Deg C | Yes
5.27 | Manufacturer / Type / country of origin - Exciter | VTA | Italy/UK/China
5.28 | Manual control setting | Required | N/A
5.29 | Automatic control setting | Required | Complied
5.30 | Steady state voltage adjuster | Required | Complied
5.31 | CT Protection Class | 5P20 | 5P20
5.32 | Differential CT [Current Transformer] | As per Vendor Standard Protection Scheme | Complied
5.33 | CT Measuring Class | Class 1 | 0.5FS5
5.34 | Voltage regulator | VTA | DER2
5.35 | Cooling method | Fan Cooling | Yes
5.36 | Installation method | IM B3 | Explanation required from buyer end
5.37 | Bearing structure | VTA | Ball bearing 6322
5.38 | Overall weight | VTA | 2140kg
5.39 | Moment of inertia | VTA | Refer to datasheet
5.40 | Parallel operation | Required | Complied
5.41 | Transient voltage adjustment rate | VTA | Refer to datasheet
5.42 | Overload Capability | VTA | 10%
5.43 | Over current Capability | VTA | Refer to datasheet
5.44 | Short-circuit current capability | VTA | Short circuit ratio 0.33
5.45 | Voltage Variation | ±10% | Complied
5.46 | Frequency Variation | ±5% | Dependes on load steps
5.47 | Terminal Boxes Separate terminal boxes shall be provided for: 1. Stator connections and Stator star point connections 2. Heater connections 3. Exciter connections 4. RTD connections 5. CT connection 6. Other connections | VTA | Alternator mounted terminal box will coprises of 1 to 6 items
5.48 | Anti-condensation Heaters | Required | Will be provided
6 | GENERATOR CONTROL PANEL
6.1 | Dimension | VTA | 650x800x1975
6.2 | Generator Breaker Make | VTA | ABB/Schnider/Equiv.
6.3 | Generator Breaker Type | ACB [Motorized] | ACB [Motorized]
6.4 | Generator Breaker Rating | Min 1250Amp | 1600
6.5 | Breaking Capacity | VTA | Refer to datasheet
6.6 | Breaker Closing Time | VTA | Refer to datasheet
6.7 | Breaker Tripping Time | VTA | Refer to datasheet
6.8 | Remote Circuit Breaker On/Off Command and Interface | Required | Complied
6.9 | Automatic Starting and Synchronization | Required | Complied
6.10 | Raise/Lower Voltage Regulator | Required | Complied
6.11 | Voltage Input Interface from Switchgear for Synchronization | Required | Complied
7 | RESISTANCE & REACTANCE
7.1 | Synchronous (Xd) - Sat & Unsat | VTA | Sat 357.7%, Unsat 431%
7.2 | Transient (X'd) | VTA | Sat 15.8%, Unsat 19.1%
7.3 | Sub transient (X''d) | VTA | Sat 7.46%, Unsat 8.99%
7.4 | Time constant of transient component（Td’） | VTA | 0.23sec
7.5 | Subtransient reactance time constant (Td") | VTA | 0.017sec
7.6 | Quadrature axis synchronous reactance (Xq） | VTA | Sat 147.3%, Unsat 177.5%
7.7 | Quadrature axis super transient reactance (Xq”) | VTA | Sat 18.5%, Unsat 22.3%
7.8 | Stator winding DC resistance (r1) | VTA | Refer to datasheet
7.9 | Time constant direct current (Ta) | VTA | 0.022 sec
7.1 | Negative Sequence Reactance (X2) | VTA | Sat 357.7%, Unsat 431%
7.11 | Parallel Operation | Required | Complied
8 | PHYSICAL CHARACTERISTICS
8.1 | GEG Set Container Dimensions (L x W x H ) in mm | VTA | 6060x2440x2590 mm
8.2 | Total Weight of the GEG Set Container (kg) | VTA | To be provided upon confirmation
8.3 | Control Panel Dimensions (L x W x H ) in mm | VTA | To be provided upon confirmation
8.4 | Control Panel IP Rating | VTA | IP42
8.5 | Dimensions (L x W x H ) in mm | VTA | To be provided upon confirmation
8.6 | Weight of Alternator (kg) | VTA | 2140kg
8.7 | Weight of Engine (kg) | VTA | 2159
8.8 | Overall Weight (kg) | VTA | 7900
8.9 | Language on Labels, Manuals and Booklets | VTA | English
9 | DEGREE OF PROTECTION
9.1 | Generator / Alternator | IP 23 | IP23
9.2 | Main Terminal Box | IP 23 | IP23
9.3 | Control Panel | IP 23 | IP23
9.4 | Generator Housing | IP 55 with TEFC enclosure (containerized) | IP55
10 | CABLE DETAILS
10.1 | Power Connection cables Internal Cables: Cu/XLPE/PVC/PVC | XLPE Insulated, Copper Conductor | Complied
10.2 | Cable entry | Bottom | Complied
11 | PROTECTION
11.1 | Over current - voltage restraint (51/51V) | Required | Available with ALL IN ONE controller
11.2 | Instantaneous Phase Over current (50) | Required | Available with ALL IN ONE controller
11.3 | Stator Earth fault (With Neutral CT) 51N | Required | Available with ALL IN ONE controller
11.4 | Under voltage (27) | Required | Available with ALL IN ONE controller
11.5 | Over voltage (59) | Required | Available with ALL IN ONE controller
11.6 | Under frequency/Over frequency (81) | Required | Available with ALL IN ONE controller
11.7 | Negative phase sequence (46) | Required | Available with ALL IN ONE controller
11.8 | Reverse Power (32) | Required | Available with ALL IN ONE controller
11.9 | Stator winding temperature (26) | Required | Available with ALL IN ONE controller
11.10 | Bearing temperature (26) | Required | Available with ALL IN ONE controller
11.11 | Phase sequence voltage relay (47) | Required | Explanation required from buyers end
11.12 | Local Emergency Stop (In Control Panel) | Required | Available with ALL IN ONE controller
11.13 | Trip Supervision Relay | Required | Available with ALL IN ONE controller
11.14 | Lockout Relay | Required | Explanation required from buyers end
11.15 | Control Circuit Supervision | Required | Explanation required from buyers end
11.16 | Other Protections | As per Vendor Standard Protection Scheme | Include in ALL IN ONE controller
11.17 | The generator protection system and trip logic shall be in line with IEEE guidelines IEEE C37.101 and IEEE C37.102. | Compliance Required | Complied
12 | ALARMS
12.1 | Stator winding temperature - high | Required | Complied
12.2 | AVR [Auto Voltage Regulator] failure | Required | Complied
12.3 | Control panel general | Required | Complied
12.4 | Hardwired alarms - DG set minor trouble, major trouble, battery charger trouble | Required | Complied
12.5 | Bearing temperature - high | Required | Alternator bearing high temp alram is available
12.6 | Lock-out general (86) | Required | Complied
12.7 | Under voltage relay (27) | Required | Complied
12.8 | Under frequency relay (81) | Required | Complied
12.9 | Over current Relay (51V) | Required | Complied
12.1 | Starting battery voltage low | Required | Complied
12.11 | DC power failure | Required | Complied
12.12 | Incomer CB fault trip relay (86-1) | Required | Complied
12.13 | Fuel low alarm level | Required | Fuel pressure low Alram
13 | METERING
13.1 | Voltmeter | Required | Available with ALL IN ONE controller and analog meter will be provided
13.2 | Frequency | Required | Available with ALL IN ONE controller
13.3 | kWH meter | Required | Available with ALL IN ONE controller
13.4 | pf Meter | Required | Available with ALL IN ONE controller
13.5 | Ammeter | Required | Available with ALL IN ONE controller and analog meter will be provided
13.6 | Running hour meter | Required | Available with ALL IN ONE controller
13.7 | kW Meter | Required | Available with ALL IN ONE controller
13.8 | kVAr Meter | Required | Available with ALL IN ONE controller
13.9 | kVAH Meter | Required | Available with ALL IN ONE controller
13.1 | kVA Meter | Required | Available with ALL IN ONE controller
14 | AC POWER DETAILS
14.1 | AC System Voltage | Required | 415V
14.2 | Variation in Supply | Required | Dependes on load steps
14.3 | Short Circuit Level | Required | Refer to datasheet
15 | BATTERY CHARGER
15.1 | Battery charger | Required | Yes
15.2 | Make | VTA | Mecc Alte or anyother Compatible brand
15.3 | Model | VTA | MAS 2024R
15.4 | Input Voltage | 230VAC | Complied
15.5 | Float Voltage Range | VTA | 24V
15.6 | Boost Voltage Range | VTA | Refer to datasheet
15.7 | Float charge current | VTA | Refer to datasheet
15.8 | Boost charge current | VTA | Refer to datasheet
16 | BATTERY
16.1 | Make | VTA | MIDAC
16.2 | Model | VTA | Hercules HSD230
16.3 | Nominal voltage | 12V | 24V
16.4 | Nominal capacity | Vendor shall size | Refer to datasheet
16.5 | Dimension of Rack | VTA | Refer to datasheet
17 | F&G SYSTEM
17.1 | Flammable Gas Detector | Required | Complied
17.2 | Flame Detector | Required | Complied
17.3 | Temperature Detector | Required | Complied
17.4 | F&G Control Panel alongwith Interface with Plant Control System & Gas Generator Control Panel | Required | Complied
18 | Local Control Panel [Located inside the Generator Container] | Required
18.1 | Control, Protection, Metering, Interface: Electrical and Control System [Hardwired, RS485 & CAN bus] | Required | Complied
18.2 | Gas Engine Driven Generators shall be interfaced to DCS and ESD system for monitoring, control and shutdown functions. Vendor shall provide hardwired and serial link interface signals for monitoring, control and shutdown functions. Interface with ESD shall be hardwired via Interposing Relay Panel. Redundant MODBUS interfacing shall be utilized for the serial communication signals. | Required | Hardwired signal available for shutdown and startup. Modbus communication is available but redundancy is not availble.
19 | Remote Control Panel [Located inside the Package Container] | Required
19.1 | Control, Interface: Control System Required (including control and monitoring equipment and engine measurements/controls) for all the components inside the Gas Generator Enclosure alongwith external fans through the HMI installed on the panel. Vendor shall furnish details, the panel shall be installed inside the substation. Vendor shall provide Redundant serial communication (RS485) for interface from Gas Generator Vendor provided LCP to Control system (UCP). | Required | Available with ALL IN ONE RS 485 Controller, but redundancy is not availble.
20.0 | Pressure Regulating Skid | Required
20.1 | Vendor shall design as per the Fuel Gas Inlet Pressure and Requirement of the Offered Unit | VTA | Will be provided
21.0 | Accoustic Enclsoure | Required | Will be provided
22.0 | AC Distribution Board [For Generator Package Internal Power Distribution] | Required | Will be provided
22.1 | Form 2 IP42 415VAC 50Hz 10kAmp 1sec 3P+4W IEC 61439 RAL 7035 | VTA | Will be provided
22.2 | Panel Rated Current shall be as per the load requirement of the Generator Auxilaries | VTA | Will be provided
23.0 | Fire Protection System | Required | Will be provided
23.1 | Required (automatic fire protection system using CO2 as the extinguishing medium) | Required | Complied
24.0 | Fuel Gas Composition | Compliance Required
24.1 | Component | Fuel Gas (mole fraction) | Complied
24.2 | H2O | 0.0000 | Complied
24.3 | Nitrogen | 0.0024 | Complied
24.4 | CO2 | 0.0575 | Complied
24.5 | H2S | 0.00005 | 20PPMv
24.6 | Methane | 0.8290 | Complied
24.7 | Ethane | 0.0942 | Complied
24.8 | Propane | 0.0143 | Complied
24.9 | n-Butane | 0.0011 | Complied
24.10 | i-Butane | 0.0008 | Complied
24.11 | n-Pentane | 0.0001 | Complied
24.12 | i-Pentane | 0.0001 | Complied
24.13 | n-Hexane | 0.0000 | Complied
24.14 | Total | 1 | Complied
25.0 | Emission Monitoring System
25.1 | PEMS for Exhaust | Optional Price shall be provided | Nox Sensors will be provided to continuously measure the Nox level
26 | Inspection And Testing
26.1 | Insulation Resistance Tests | Required | Complied
26.2 | Hydrostatic Testing | Required | Complied
26.3 | Load Test | Required | Complied
26.4 | Dynamic Load Test | Required | Complied
26.5 | FAT: Factory Acceptance Test | Required | Complied
26.6 | SAT: Site Acceptance Test | Required | Complied
27 | SPARE PARTS & SPECIAL TOOLS
27.1 | Pre-commissioning/Commissioning/Start up spares Vendor to provide, Start-up & Commissioning Spares: As recommended by Vendor with item wise quantity and price break up (To be ordered with the equipment). As a minimum shall include 200% gaskets & 10% bolting (minimum 2 nos. Bolts/4 nuts per size) shall be provided per gasketted internal & external joints (for nozzles with B/F). | Required | will be provided
27.2 | Two Years Operation Spares | Optional Price shall be provided | Will be provided
27.3 | Special Tools and Tackles for Erection, Pre-commissioning, Commissioning & Operation (if applicable) | Vendor to Furnish | Yes (if any)
27.4 | A list of special tools necessary to dismantle the GEG | Vendor to Furnish | Yes (if any)
28 | OTHER REQUIREMENTS
28.1 | Guarantee / Warranty (Months) | 12 Months after commissioning | Complied
28.2 | Training Manual & Installation Operation, Maintenance Manuals | Required | will be provided
28.3 | Supervision for Commissioning at site | Per diem rates | As per KAN Standards
28.4 | Delivery location | Construction Site, UAE | UAE Jebel Ali
28.5 | Delivery Duration from Purchase Order placed date | VTA | 24-28 weeks subject to the availability of the Engine & Alternator from the OEM.
28.6 | Fabrication / Inspection & Test Location | Vendor to Furnish | Italy
28.7 | Local Agent Details | Vendor to Furnish | Bricklinx FZ LLC
28.8 | Vendor's Engineering & Procurement Location | Vendor to Furnish | Pakistan
28.9 | Preservation | Preservation suitable for 6 months storage in marine, hot and humid saline atmosphere | Seaworthy Packaging will be provided
28.10 | Vendor shall supply Gas Engine Generator (including accessories) in assembled condition. Bidder to confirm. | Compliance Required | Complied
28.11 | Painting As stated above, Before shipment, all equipment's and components of the unit shall be Facility Painted to international standards, marine grade suitable for humid, dusty and saline site conditions | Required | Complied
29 | MISCELLANEOUS
29.1 | Foundation Load Data | VTA | will be provided
29.2 | Installation/fixing detail with Foundation | VTA | will be provided
29.3 | Documents Required with Offer Filled and Complied this Data Sheet Detailed Vendor Standard Datasheet of all components Vendor & Sub-Vendor List with port of origin Heat & Material Balance Diagram PID Equipment List Power Auxiliary List Consumption List Equipment Vendor Standard Catalogs MTC and Certificates Once technical closure is recieved signed stamped this datasheet | Vendor shall submit with Offer | Will be provided later on
29.4 | Anchor Bolt | Required | Not Required
29.5 | Painting: As per Vendor Standard | VTA | As per OEM Standards
29.6 | Internal and External Earthing Container shall be provided with internal earthing with suitably designed earth bars alongwith earthing cables, point for generator star earthing, external enclosure earthing ensuring safe and reliable operation | Required | Earthing Terminals will be provided along with the container
29.7 | Auxiliary Load, kW | Required | 65KW
VTA: Vendor to Advise [With Offer]

## Emission Data
ADNOC GAS DBOOM WORKS FOR RENTAL COMPRESSION FACILITIES FOR BUHASA PLANT (PROJECT 5.0)
| ADNOC DOCUMENT NO: DOD-30201-50150-BH-000-16-00-004 CONTRACTOR DOCUMENT NO: ADN-AEC-EL-DAT-009 |  | Rev.: A
DATASHEET - GAS POWER GENERATOR
Emissions Data For Compliance
Emission Limits for Combustion Unit below 10MW Total thermal input
Sr. No. | Common Name | Chemical Symbol | Liquid Fuel | Fuel Gas or Natural Gas
|  |  | Limit Value (mg/Nm3) | Limit Value (mg/Nm3)
1 | Oxides of Nitrogen (Complied) | Nox | 200 | 100 (Natural Gas) 200 (Fuel Gas)
2 | Particulate Matter (Complied But we will be unable to perform test on site) | PM | 30 | 10
3 | Sulphur Dioxide (Not Complied) | SO2 | 350 | 35
4 | Cabon Monoxide (Complied) | CO | 50 | 50
Note: Reference Conditions 273K, dry, 101.3kPa and 3% O2