## Cover Sheet
ADNOC GAS DEFINE STAGE PROJECT CONTRACT No. 4700024157 PROJECT No. 5.0 (P5)
MR FOR GAS POWER GENERATOR
DOCUMENT NO. ADN-AEC-ME-SPC-026
0 | 2024-10-10 | HS | WJ | AA | ISSUED FOR QUOTATION
REV | DATE | PREPARED | REVIEWED | APPROVED | DESCRIPTION
THIS DOCUMENT IS INTENDED FOR USE BY ADNOC ONSHORE AND ITS NOMINATED CONSULTANTS, CONTRACTORS, MANUFACTURERES AND SUPPLIERS
DOCUMENT NO. DOD-30210-50150-BH-000-10-00-009 |  |  |  |  | PAGE 1 OF 6
ADNOC CONTRACT NO. 4700024157 |  |  | PROJECT NO. AP-044 | CLASS 1 | DATE: 10-10-2024

## Notes
PROJECT: | AP-044 | ADNOC GAS DEFINE STAGE PROJECT 5.0 (P5)
ADNOC CONTRACT NO: | 4700022685
DOC. No: | ADN-AEC-ME-SPC-026 | MR FOR GAS POWER GENERATOR
REV NO. | 0
(A) Preamble
SL. No. | Description
1 | INTRODUCTION:
ADNOC is aiming to increase oil production to produce 5.0 MMBOPD by year-end 2027. Accordingly, associated gas production is anticipated to increase. Hence, the overall gas supply scenarios for major ADNOC Gas (hereafter referred to as COMPANY) assets i.e., Das Facilities, Bab and Habshan Complex (Habshan 0, 1, 2, 4, and 5), Asab and Bu Hasa, is anticipated to change depending on their feed sources, profiles including rates, compositions, and operating conditions. COMPANY’s permanent facilities to accommodate increased gas supply by 2027 will be achieved through long term EPC Contract. As the permanent facilities will only be ready by year 2027, COMPANY intends to exercise the short-term solutions (Rental Compressor and corresponding Balance of Plant (BOP)) for Buhasa plant to accommodate peak gas flow and ensure bottlenecks in years 2025, 2026 and 2027 are mitigated, prior to implementation of a long-term solution that caters the entire production profile.
2 | PROJECT OBJECTIVE
The short-term solution includes Rental Compressor (By ‘Design Built Own Operate and Maintain’ - DBOOM Contractor) and corresponding Balance of Plant (BOP) works for impacted COMPANY facilities is as follows. DBOOM Scope – Design, Build, Own, Operate and Maintain (DBOOM) the Rental Compression facility including required utility to process additional gas from Buhasa P5 facility. The scope includes detailed engineering, procurement & supply, installation & testing, Commissioning and Operation & Maintenance works. BOP Scope – The Balance of Plant (BOP) facility to interface and hook up the rental compressors to the main plant production stream including New LP and IP Pipelines with associated engineering. The COMPANY shall execute the separate contract for this Scope.
3 | PURPOSE OF THIS DOCUMENT
The purpose of this document is to define the minimum requirements for the Design, Engineering, Material Procurement Manufacture / Fabrication, Assembly, Testing, Inspection, Performance Testing, Painting, Documentation, Transportation Packing, Forwarding and Commissioning of GAS ENGINE DRIVEN GENERATORs for the P5 Project. This document along with the referenced documents and standards are binding and are to be complied by the VENDOR. Also VENDOR shall make an unequivocal statement that the GAS ENGINE DRIVEN GENERATORs offered are approved for Installation in Abu Dhabi, UAE.
4 | SYSTEM DESCRIPTION
P5 Compression Facility shall be fed from the natural gas generator [GEG] G-4101-01A & G-4101-01B and one number emergency diesel generator. a. During normal operation, one of the GEG shall run and feed power to the facility. b. If a failure occurs during a normal operation, the EDG shall be switched on. c. GEG-2 shall be switched and synchronized with edg and once synchronized. d. Any generator running parallel shall be synchronized prior to the parallel operation, this shall be made sure by the generator vendor with his control system.
5 | VENDOR SCOPE OF SUPPLY
Vendor shall supply Gas Engine Driven Generator set with Control system, Cooling system, Connection to natural gas system, Generator set accessories, Mounting system, Base slab and vibration isolation, Controller Panels alongwith synchronization relays, Weatherproof housing and all other accessories to complete the power generation requirement mentioned in the detailed requirements below. 0.525 MW, 415V, 3Phase, 50Hz, Containerized type Gas Engine Generator - 2 Nos.
6 | LIST OF APPLICABLE INTERNATIONAL STANDARDS
| STANDARD REFERENCE |  |  | Compliance | Vendor Response | Remarks
| ANSI AWS D1.1/D1.1M |  | Structural Welding Code - Steel | Required
| BS 4999-140 |  | General requirements for rotating electrical machines Part 140. Voltage regulation and parallel operation of A.C. synchronous generators | Required
| IEC 60034 (part 1, 5, 6, 8) |  | Rotating Electrical Machines | Required
| IEC 60071-1 |  | Insulation co-ordination – Part 1: Definitions, principles and rules | Required
| IEC 60255 |  | Measuring relays and protection equipment | Required
| IEC 60445 |  | Basic and safety principles for man-machine interface, marking and identification – Identification of equipment terminals, conductor terminations and conductors | Required
| IEC 60529 |  | Degrees of protection provided by enclosures (IP code) | Required
| IEC 60898 |  | Electrical accessories - Circuit-breakers for overcurrent protection for household and similar installations | Required
| IEC 61850 |  | Communication networks and systems in substations | Required
| IEC 61869 (part 1, 2, 3) |  | Instrument transformers | Required
| ISO 1813 |  | Belt drives. V-ribbed belts, joined V-belts and V- belts including wide section belts and hexagonal belts. Electrical conductivity of antistatic belts: Characteristics and methods of test | Required
| ISO 3046-(part 1, 4) |  | Reciprocating Internal Combustion Engines | Required
| ISO 8528 |  | Reciprocating Internal Combustion Engine Driven Alternating Current Generating Sets | Required
| ISO 10816-(part 1, 5) |  | Mechanical vibration – Evaluation of machine vibration by measurements on nonrotating parts | Required
| ISO 10816-6 |  | Part 6: Reciprocating machines with power ratings above 100 kW | Required
| ASCE 7-05 |  | Minimum Design Loads for Building and Other Structures | Required
| AISC 325 |  | Steel Construction Manual | Required
| AISC 341 |  | Seismic Provisioning for Steel Buildings | Required
| Refer "Attachment-4 Applicable Codes and Standards" for the full list |  |  | Required
7 | LIST OF ATTACHMENTS
| Attachment-1A Fuel Gas_Sus_Summer |  |  | Required
| Attachment-1B Fuel Gas_Sus_Winter |  |  | Required
| Attachment-2 Emission Compliance Data |  |  | Required
| Attachment-3 Synchronization Diagram |  |  | Required
| Attachment-4 Applicable Codes and Standards |  |  | Required
| Attachment-5 Approved Vendor List 21.05.2024 |  |  | Required
| Attachment-6 Technical Deviation |  |  | Required
| Attachment-7 Load List |  |  | Required
| Attachment-8 Typical Gas Generators IO List |  |  | Required
| Attachment-9 VDRL |  |  | Required

## Table 1
MR FOR GAS POWER GENERATOR
SL. NO. | DESCRIPTION | UNIT | PROJECT REQUIREMENTS | VENDOR COMPLIANCE (CONFIRMED / NOT CONFIRMED) | CONTRACTOR REMARKS | CLIENT REMARKS | REMARKS
1 | GENERAL
1.1 | Generator Rating | - | 525kW, 415V, 3Phase, 4Wire, 50Hz, Containerized type Gas Engine Generator - 2 Nos. Star Connection, Duty S1, | Confirmed
1.2 | Temperature | 5-58 deg C | Vendor to confirm compliance | Confirmed
1.3 | Design Life | - | 05 years; Bidder to comply | Confirmed
1.4 | Vendor Deviation Form as per Attachment-6 | - | Signed / Stamped copy is required with Offer Any deviations from the PROJECT requirements shall be listed in Attachment- 6. Deviations listed elsewhere will not be considered for evaluation | Confirmed
1.5 | Tag No's |  | G-4101-01A & G-4101-01B | Confirmed
1.6 | Weight | kg | Vendor to Furnish | 7900 Kg
1.7 | Compliance to IEC 60034 | - | Required | Confirmed
1.8 | Vendor & Sub-Vendors (Vendor of all items in scope) to be as per COMPANY Approved Vendor List | As per the Attachment-5 Approved Vendor List | Vendor to Confirm. | Confirmed
1.9 | Hazardous Area Classification | - | Safe Area | Confirmed
1.10 | Anchor Bolt |  | Required | Confirmed (Will be provided only)
1.11 | Manufacturer | - | Vendor to Furnish | KAN
1.12 | Model No. | - | Vendor to Furnish | As per KAN Nameplate
1.13 | Country of Origin | - | Vendor to Furnish | Italy
1.14 | Foundation Load Data |  | Vendor to Furnish | Will be provided
1.15 | Installation/fixing detail with Foundation |  | Vendor to Furnish | Will be provided
1.16 | Documents Required with Offer |  | Filled and Complied This MR Sheet Detailed Vendor Standard Datasheet of all components Vendor & Sub-Vendor List with port of origin Heat & Material Balance Diagram PID Equipment List Power Auxiliary List Consumption List Equipment Vendor Standard Catalogs MTC and Certificates Once technical closure is recieved signed stamped this MR Sheet | Will be provided
2 | Technical Requirements & Scope of Supply
2.1 | Alternator | - | Vendor to Furnish | MeccAlte EC043 2S4A
2.2 | Acoustic Enclosure with complete package skid | - | Required with cooling fans Enclosure shall be strong enough to withstand the CO2 release and corresponding CO2 thermal expansion | Confirmed
2.3 | Starting System | - | Vendor to Furnish | Electrical
2.4 | Lube Oil System | - | Vendor to Furnish | Positive pressure lubrication system
2.5 | Generator Duty Type | - | S1 according to IEC 60034-1 | confirmed
2.6 | Generator Insulation Temperature | - | Class F and to Class B temperature rise | Confirmed
2.7 | Generator Winding Insulation |  | Class H | Confirmed
2.8 | Installation requirement | - | Outdoor Installation in Containerized | Confirmed
2.9 | Fire & Gas System | - | F&G Detector Requirement 1. Flammable gas detection on the combustion and ventilation air inlet- Minimum 3 quantity 2. Gas detection on the ventilation air inlet -Minimum 3 quantity 3. Flame Detector at Enclosure including Load Compartment 4. Rise of Heat Detector at Enclosure including Load Compartment 5. Fire and Gas Beacon alarm & Horn - outside Enclosure Detector design The F&G devices shall be of minimum SIL 2 certified | Confirmed
2.10 | Fire Protection System | - | Required (automatic fire protection system using CO2 as the extinguishing medium | Confirmed
2.11 | Enclosure Temperature monitoring system | - | Required | Confirmed
2.12 | Sustained Overload | - | Generator shall be capable of carrying a stator current of 110% of the rated current for a period of at least one hour at rated voltage, frequency and power factor. | Confirmed
2.13 | AVR | - | Required (microprocessor based) | Confirmed
2.14 | Voltage Variation | % | ±10% | Confirmed
2.15 | Frequency Variation | % | ±5% | Confirmed
2.16 | Power Factor | - | 0.8 lagging | Confirmed
2.17 | I2t | - | Vendor to Furnish | Confirmed
2.18 | Electromagnetic Compatibility | - | Accordance to IEC 61000 | Confirmed
2.19 | Starting Batteries | - | Required | Confirmed
2.20 | Type of Batteries | - | As per Manufacturer standard | Confirmed
2.21 | Battery Charger | - | Required | Confirmed
2.22 | Rating Plate | - | Required | Confirmed
2.23 | Efficiency (50 %, 75 %, and 100 % rated output) | - | Vendor to Furnish | Confirmed (refer to data sheet)
2.24 | Generator Cooling | - | Air Cooling or Liquid Cooling (Air cooling is preferred) Vendor shall include the number of fans and wattage | Confirmed
2.25 | Generator Housing | - | IP 55 with TEFC enclosure (containerized) | Confirmed
2.26 | Neutral Earthing | - | Solidly Earthed for LV System | Confirmed
2.27 | Direction of rotation | - | IEC 60034-8 | Confirmed
2.28 | RTD | - | PT100 RTD, 2 per phase (RTDs shall be connected to the DCS) | PT100 will be provided (two on each phase)
2.29 | Terminal Boxes | - | Separate terminal boxes shall be provided for: 1. Stator connections and Stator star point connections 2. Heater connections 3. Exciter connections 4. RTD connections 5. CT connection 6. Other connections | Alternator mounted terminal box will coprises of 1 to 6 items
2.30 | Frequency stability | - | Governing class A2 | Confirmed
2.31 | Gas engine | - | Vendor to Furnish | Confirmed
2.32 | Air Intake System with filter and DPI and Wild-run shutdown valve | - | Vendor to Furnish (shall be part of the skid package)
2.33 | Engine Exhaust System with Silencer | - | Vendor to Furnish | Confirmed
2.34 | Terminal Boxes | - | Vendor to Furnish | Confirmed
2.35 | Engine Cooling System | - | Vendor to Furnish | Air Cooled Horizontal Radiator
2.36 | Shaft Couplings | - | Required | Direct Coupled
2.37 | Torsional Analysis of Engine | - | Required | Torsion vibration compatability will be provided later on upon finalization
2.38 | Excitation system | - | Brushless type, consisting of a main AC Exciter and a permanent magnet generator direct coupled and air cooled | Self Excited with PMG
2.39 | Excitation - Rated Current | - | At least 110% of the excitation current at the rated output of the generator under the most stringent operating conditions | Confirmed
2.40 | Excitation - Rated Voltage | - | At least 110% of the rotor voltage at the rated output of the generator under the most stringent conditions | Confirmed
2.41 | Replacement interval of the lubricating oil | - | Vendor to Furnish
2.42 | Noise Limit | dBA | 85dB(A) at 1 meter distance | Confirmed
2.43 | Auxiliary Load Requirement | - | Vendor to Furnish
2.44 | Anti-condensation Heaters | - | Required | Will be provided
2.45 | Engine and Generator Painting | - | As per Manufacturer standard | Confirmed
2.46 | Generators Synchronization | - | Generator synchronization relays shall be provided by Generator vendor as per attached Synchronization Scheme | Confirmed
2.47 | Gas Pressure Regulating Skid | - | Generator synchronization relays shall be provided by Generator vendor as per attached Synchronization Scheme | Confirmed
2.48 | The generator protection system and trip logic shall be in line with IEEE guidelines IEEE C37.101 and IEEE C37.102. | - | Vendor to confirm compliance | Confirmed
2.49 | Internal and External Earthing | - | Container shall be provided with internal earthing with suitably designed earth bars alongwith earthing cables, point for generator star earthing, external enclosure earthing ensuring safe and reliable operation | Earthing Terminals will be provided along with the container
2.50 | Internal Lighting | - | Container shall be provided with internal lighting and external bulk head lighting on the doors | Confirmed
2.51 | Selective Catalytic Reduction system (SCR) | Optional Price | Vendor shall include the price based on the overall design and compliance to the project emission requirement | Not Confirmed
2.52 | Gas Genset Auxiliary Load | Refer to the attached Load List. Vendor shall review the load list and confirm the starting of the largest motor at star-delta configuration | Vendor to confirm compliance | Confirmed
2.5 | Gas Composition Data | Attachment-1A Fuel Gas_Sus_Summer Attachment-1B Fuel Gas_Sus_Winter | Vendor to confirm compliance | Complied
2.5.1 | H2S Content | 700 ppm | Vendor to confirm compliance | Not Confirmed
2.6 | Inlet Gas Supply
2.6.1 | Pressure | Attachment-1A Fuel Gas_Sus_Summer Attachment-1B Fuel Gas_Sus_Winter | Vendor to confirm compliance | Confirmed
2.6.2 | Temperature | Attachment-1A Fuel Gas_Sus_Summer Attachment-1B Fuel Gas_Sus_Winter | Vendor to confirm compliance | Confirmed
2.7 | Ambient requirements
2.7.1 | For Gas Engine generator set | 4-58 deg C | Vendor to confirm compliance | 5-58 deg C
2.8 | Gas type
2.8.1 | Biogas or Natural Gas | Dry Gas | Vendor to confirm compliance | Natural Gas
2.8.2 | Emission Data | Compliance with Emission limits as per local regulation. Refer Attachment-2 Emission Compliance Data | Vendor to confirm compliance | Not Confirmed
2.8.3 | Emission Control Equipment | As required | Vendor to confirm as per the Emission Data requirement
2.9 | Applicable Codes and Standards | Attachment-4 Applicable Codes and Standards | Vendor to confirm compliance | Not Confirmed
3 | Control and Protection Requirement
3.1 | Local Engine Control Panel (LCP) Placed inside the Gas Generator Container | - | Required, 1. Protection, control and metering equipment 2. AVR 3. Complete AC sub-distribution for the generator space heater, panel space heater and any other generator auxiliary items 4. Raise/lower voltage adjuster (behind the panel door) 5. Generator status, alarm and trip functions 6. Automatic starting / synchronizing facilities with manual override, synchroscope and synchronizing lamps 7. Control of switchgear remote generator CB 8. Control gear for generator set auxiliaries 9. Control relays (under-voltage, etc…) 10. Battery backed up DC power supply distribution for the generator protection systems (may be combined with the engine protection systems) 11. Generator testing facility 12. Winding/bearing temperature monitoring facility Vendor shall provide Redundant serial communication (RS485) for interface from Gas Generator Vendor provided LCP to Control system (UCP). 13. Fire Alarm & Detection and Fire Fighting System Equipment, Panel and Interface. 14. Gas Generator Enclosure external fans power and control panel supply with builtin contactors and external cooler temperature interface. | Need further discussion and Explanation
3.2 | Remote Generator Control Panel (GCP) Placed inside the Substation | - | Required (including control and monitoring equipment and engine measurements/controls) for all the components inside the Gas Generator Enclosure alongwith external fans through the HMI installed on the panel. Vendor shall furnish details, the panel shall be installed inside the substation. Vendor shall provide Redundant serial communication (RS485) for interface from Gas Generator Vendor provided LCP to Control system (UCP). | Available with ALL IN ONE RS 485 Controller, but redundancy is not availble.
3.3 | Protective Devices | - | All protective relays shall be of microprocessor type. The following electrical protective relays shall be provided as minimum to protect the generator. a. Reverse power (32) b. Stator winding over temperature (49) c. Time delay zero sequence over current (51N) d. Time delay voltage restrained over current (51V) e. Synchro check relay (25) f. Undervoltage relay (46) g. Negative phase sequence relay (46) h. Lockout relay (86) i. Over voltage protection (59) j. Field failure protection (loss of excitation) (40) k. Diode failure protection l. Trip circuit supervision relay (96) m. Instantaneous over current relay (50) n. Rotor earth fault (64R) o. Stator earth fault (64S) p. Frequency relay (81) q. Restricted Earth Fault Protection (87N) r. Differential Protection for Generator (87G) | Diode failure protection,Trip circuit supervision relay (96),Rotor earth fault (64R), Stator earth fault (64S), q. Restricted Earth Fault Protection (87N), Differential Protection for Generator (87G) Are not available
3.4 | Interface with DCS & ESD |  | Gas Engine Driven Generators shall be interfaced to DCS and ESD system for monitoring, control and shutdown functions. Vendor shall provide hardwired and serial link interface signals for monitoring, control and shutdown functions. Interface with ESD shall be hardwired via Interposing Relay Panel MODBUS interfacing shall be utilized for the serial communication signals | Hardwired signal available for shutdown and startup. Modbus communication is available but redundancy is not availble.
3.5 | On-line testing facility | - | Required for Generator | Not Confirmed
3.6 | Emergency Shut down facility including the shutdown valve and required control valves shall be provided as part of the package | - | Required | Confirmed
3.7 | Internal Wiring and Terminations | - | Vendor to provide | Confirmed
3.8 | Panel Painting | - | As per MANUFACTURER's standard | Confirmed
3.9 | Instrument Specification | - | As per MANUFACTURER's standard | Confirmed
3.1 | Earthing | - | Vendor to provide a busbar connecting all the conducting material properly earthed with adequate earth cable on the skid baseplate. | Confirmed
3.11 | Internal Triping | - | Vendor shall consider internal Tripping signal and control signals within LCP. | Not Confirmed
4 | COMPLIANCE TO INTERNATIONAL STANDARDS
4.1 | IEC, BS & NFPA, NEMA | - | Required | Confirmed
5 | GENERAL REQUIREMENTS
5.1 | Quality and Vendor data Requirements | - | As per VDRL | Not Confirmed
5.2 | Painting | - | As stated above, Before shipment, all equipment's and components of the unit shall be Facility Painted to international standards, marine grade suitable for humid, dusty and saline site conditions, | Confirmed
6 | INSPECTION AND TESTING
6.1 | Insulation Resistance Tests | - | Required | Confirmed
6.2 | Hydrostatic Testing | - | Required | Confirmed
6.3 | Load Test | - | Required | Confirmed
6.4 | Dynamic Load Test | - | Required | Confirmed
6.5 | FAT | - | Required | Confirmed
6.7 | On Site Tests (SAT) | - | Required | Confirmed
7 | DOCUMENTATION
7.1 | Documentation | - | As per VDRL | Will be provided later upon finalization and issuance of LOI
7.2 | Language | - | English | Confirmed
7.3 | VENDOR Document Requirement - VDRL | Attachment-09 VDRL This list represents the minimum list of documents. Vendor shall include all required for manufacturing and document which are deemed necessary for quality control and comissioning | Vendor to confirm compliance | Will be provided later upon finalization and issuance of LOI
8 | SPARE PARTS & SPECIAL TOOLS
8.1 | Pre-commissioning/ Commissioning / Start up spares | - | Required / Vendor to provide, Start-up & Commissioning Spares : As recommended by Vendor with item wise quantity and price break up (To be ordered with the equipment). As a minimum shall include 200% gaskets & 10% bolting (minimum 2 nos. Bolts/4 nuts per size) shall be provided per gasketted internal & external joints (for nozzles with B/F). | Will be Provided
8.2 | Two Years Operation Spares | - | Required - List in SPIR Form to be submitted | Will be Provided
8.3 | Special Tools and Tackles for Erection, Pre-commissioning, Commissioning & Operation (if applicable) | - | Vendor to Furnish | Yes (If any)
8.4 | A list of special tools necessary to dismantle the GEG | - | Vendor to Furnish | Yes (If any)
9 | OTHER REQUIREMENTS
9.1 | Guarantee / Warranty (Months) | - | Complied | Complied
9.2 | Training Manual & Installation Operation, Maintenance Manuals | - | Required | Will be Provided
9.3 | Supervision for Commissioning at site | - | Per diem rates | As per KAN standards
9.4 | Delivery location | - | Construction Site, UAE | UAE Jebel Ali
9.5 | Delivery Duration from Purchase Order placed date | weeks | VTA | 24-28 weeks subject to the availability of the Engine & Alternator from the OEM.
9.6 | Fabrication / Inspection & Test Location | - | Vendor to Furnish | Italy
9.7 | Local Agent Details | - | Vendor to Furnish | Bricklinx FZ LLC
9.8 | Vendor's Engineering & Procurement Location | - | Vendor to Furnish | Pakistan
9.9 | Preservation | - | Preservation suitable for 6 months storage in marine, hot and humid saline atmosphere | Seaworthy Packaging will be provided
9.1 | Vendor shall supply Gas Engine Generator (including accessories) in assembled condition. Bidder to confirm. | - | Required | Confirmed
ABBREVIATIONS :
VTA: Vendor to advise
TBA:- To be advised
VTC: Vendor to comply
VTF: Vendor to furnish
NA: Not Applicable
MOC: Material of Construction